## Cover Sheet
Rural Distribution Transformer supplied by an HV Overhead Line
HB 219 Worked Example 3.2.2
Rural network, aerial HV feed to pole-mounted distribution transformer supplying a single customer, no OHEW, common HV/LV earth, LV neutral not bonded to HV source substation
HV single phase-to-earth fault at the distribution transformer
HV Fault Source Data
HV phase - neutral voltage | 12702 | V
Single phase fault level | 400 | MVA
HV Overhead Line Data
Conductor size | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | 10 | km
Positive sequence line impedance | 0.2722 | + j | 0.3407 | W / km
Zero sequence line impedance | 0.4204 | + j | 1.6545 | W / km
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 0 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Description of distribution transformer earthmat | 2 x 2m earth rods (14mm dia.) at 2m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance formula | Re = | 0.19 | r
Description of customer electrode | 1 x 1.2m earth rod (12mm dia.)
Customer single earth rod earth resistance formula | Rc = | 0.75 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance
3. The impedance of the LV distribution line neutral conductor is negligable compared to the resistance of the customer single electrode.
Calculated Values
Equivalent hemispherical radius of the distribution transformer earthmat |  |  |  | 0.83766 | m
Equivalent hemispherical radius of the customer electrode |  |  |  | 0.21221 | m
Fault current (returning through the earth) |  |  |  | 1249.0142 | A
EPR on the distribution transformer earthmat |  |  |  | 1893.4523 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault at the distribution transformer
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 12702 | V
Single phase fault level | S = | 400 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 1.21005603j | Ω |  | 1.2101
Negative sequence source impedance | ZS2 = | ZS1 | = | 1.21005603j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 1.21005603j | Ω
HV Overhead Line Data
Conductor Size |  | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | L = | 10 | km
Positive sequence line impedance | ZL1 = | 0.2722+0.3407j |  | W / km
Negative sequence line impedance | ZL2 = | ZL1 = | 0.2722+0.3407j |  | W / km
Zero sequence line impedance | ZL0 = | 0.4204+1.6545j |  | W / km
NER and Earth Impedances
Neutral Earthing Resistor resistance |  | ZNER = | 0 | Ω
Zone Substation earthmat resistance |  | RZS = | 0.01 | Ω
Surface soil resistivity |  | r = | 10 | Ω - m
Description of distribution transformer earthmat |  | 2 x 2m earth rods (14mm dia.) at 2m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance |  | Re = | 0.19 | r
|  | = | 1.9 | Ω
Equivalent Hemispherical Radius |  | rE =
|  | = | 0.83766 | m
Description of customer electrode |  | 1 x 1.2m earth rod (12mm dia.)
Customer single earth rod earth resistance |  | Rc = | 0.75 | r
|  | = | 7.5 | Ω
Equivalent Hemispherical Radius of the customers electrode |  | rE =
|  | = | 0.21221 | m
Equivalent MEN plus Re impedance |  | Req =
|  | = | 1.516 | Ω
Network Impedances
Sequence network impedances | Zpos = | ZS1 + ZL1.L
| = | 2.722+4.61705603j |  | Ω
| Zneg = | ZS2 + ZL2.L
| = | 2.722+4.61705603j |  | Ω
| Zzero = | ZS0 + ZL0.L + 3.Req + 3.Rzs
| = | 8.78187234042553+17.75505603j |  |  | Ω
Fault Current
Zero sequence fault current (returning through the earth) | I0 =
Fault current (returning through the earth) | If = | 3.I0
| = | 582.398521484784-1104.9200509872j |  |  |  | A
| │If │ = | 1249.0142 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Req
| = | 1893.4523 | V