## Cover Sheet
Fault to 11kV Concrete or Steel Pole
HB 219 Worked Example 3.3.1
11 kV source. No NER. No OHEW. 5km aerial 11 kV line.
11kV single phase-to-earth fault to a concrete or steel pole
HV Fault Source Data
HV phase - neutral voltage | 6350 | V
Single phase fault level | 200 | MVA
HV Overhead Line Data
Conductor Size | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | 5 | km
Positive sequence line impedance | 0.2722 | + j | 0.3407 | W
Zero sequence line impedance | 0.4204 | + j | 1.6545 | W
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 0 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Description of pole footing | Pole 300mm diameter buried 1.525m deep in the soil
Pole footing earth resistance formula | Re = | 0.309 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance
Calculated Values
Equivalent hemispherical radius of the pole footing |  |  |  | 0.51506 | m
Fault current (returning through the earth) |  |  |  | 975.2245 | A
EPR on the pole |  |  |  | 3013.4437 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault to a concrete or steel pole
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 6350 | V
Single phase fault level | S = | 200 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 0.6048375j | Ω |  | 0.60484
Negative sequence source impedance | ZS2 = | ZS1 | = | 0.6048375j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 0.6048375j | Ω
HV Overhead Line Data
Conductor Size |  | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | L = | 5 | km
Positive sequence line impedance | ZL1 = | 0.2722+0.3407j |  | Ω/km
Negative sequence line impedance | ZL2 = | ZL1 = | 0.2722+0.3407j |  | Ω/km
Zero sequence line impedance | ZL0 = | 0.4204+1.6545j |  | Ω/km
NER and Earth Impedances
Neutral Earthing Resistor resistance |  | ZNER = | 0 | Ω
Zone Substation earthmat resistance |  | RZS = | 0.01 | Ω
Surface soil resistivity |  | r = | 10 | Ω - m
Description of pole footing |  | Pole 300mm diameter buried 1.525m deep in the soil
Pole footing earth resistance |  | Rp = | 0.309 | r
|  | = | 3.09 | Ω
Equivalent hemispherical radius of pole footing |  | rE =
|  | = | 0.51506 | m
Network Impedances
Sequence network Impedance | Zpos = | ZS1 + ZL1.L
| = | 1.361+2.3083375j |  | Ω
| Zneg = | ZS2 + ZL2.L
| = | 1.361+2.3083375j |  | Ω
| Zzero = | ZS0 + ZL0.L + 3.Rp + 3.Rzs
| = | 11.402+8.8773375j |  | Ω
Fault Current
Zero sequence fault current (returning through the earth) | I0 =
Fault current (returning through the earth) | If = | 3.I0
| = | 705.13443387906-673.682587435884j |  |  |  | A
| │If │ = | 975.2245 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Rp
| = | 3013.4437 | V