## Cover Sheet
Fault to 33kV Concrete or Steel Pole
HB 219 Worked Example 3.4.2
33 kV source. 20 ohm NER. No OHEW. 10 km aerial 33 kV line.
33kV single phase-to-earth fault to a concrete or steel pole
HV Fault Source Data
HV phase - neutral voltage | 19053 | V
Single phase fault level | 500 | MVA
HV Overhead Line Data
Conductor Size | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | 10 | km
Positive sequence line impedance | 0.2722 | + j | 0.3479 | W
Zero sequence line impedance | 0.4204 | + j | 1.5748 | W
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 20 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Description of pole footing | Pole 500 mm diameter buried 2.0 m deep in the soil
Pole footing earth resistance formula | Re = | 0.17 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance
Calculated Values
Equivalent hemispherical radius of the pole footing |  |  |  | 0.93621 | m
Fault current (returning through the earth) |  |  |  | 711.8925 | A
EPR on the pole |  |  |  | 1210.2172 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault to a concrete or steel pole
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 19053 | V
Single phase fault level | S = | 500 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 2.178100854j | Ω |  | 2.1781
Negative sequence source impedance | ZS2 = | ZS1 | = | 2.178100854j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 2.178100854j | Ω
HV Overhead Line Data
Conductor Size |  | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | L = | 10 | km
Positive sequence line impedance | ZL1 = | 0.2722+0.3479j |  | Ω/km
Negative sequence line impedance | ZL2 = | ZL1 = | 0.2722+0.3479j |  | Ω/km
Zero sequence line impedance | ZL0 = | 0.4204+1.5748j |  | Ω/km
NER and Earth Impedances
Neutral Earthing Resistor resistance |  | ZNER = | 20 | Ω
Zone Substation earthmat resistance |  | RZS = | 0.01 | Ω
Surface soil resistivity |  | r = | 10 | Ω - m
Description of pole footing |  | Pole 500 mm diameter buried 2.0 m deep in the soil
Pole footing earth resistance |  | Rp = | 0.17 | r
|  | = | 1.7 | Ω
Equivalent hemispherical radius of pole footing |  | rE =
|  | = | 0.93621 | m
Network Impedances
Sequence network Impedance | Zpos = | ZS1 + ZL1.L
| = | 2.722+5.657100854j |  | Ω
| Zneg = | ZS2 + ZL2.L
| = | 2.722+5.657100854j |  | Ω
| Zzero = | ZS0 + ZL0.L + 3.Rp + 3.Rzs
| = | 9.334+17.926100854j |  | Ω
Fault Current
Zero sequence fault current (returning through the earth) | I0 =
Fault current (returning through the earth) | If = | 3.I0
| = | 663.006832416003-259.254331227329j |  |  |  | A
| │If │ = | 711.8925 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Rp
| = | 1210.2172 | V