## Cover Sheet
Isolated Urban MEN System (New Subdivision) supplied by an HV Overhead Line
HB 219 Worked Example 3.5.1
Urban network, new subdivision, isolated MEN with 48 customers, 500m underground cable feed from 2km aerial HV line to a pad mounted distribution transformer, no OHEW, common HV/LV earth, LV neutral not bonded to HV source zone substation.
Supply to underground subdivision. HV single phase-to-earth fault at the pad mounted distribution transformer.
HV Fault Source Data
HV phase - neutral voltage | 6350 | V
Single phase fault level | 200 | MVA
HV Overhead Line Data
Conductor Size | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | 2 | km
Positive sequence line impedance | 0.2722 | + j | 0.3407 | W / km
Zero sequence line impedance | 0.4204 | + j | 1.6545 | W / km
HV Cable Data
Cable size and type | 150 sqmm Al Belted PILCPS
Length | 0.5 | km
Positive sequence cable impedance | 0.2078 | + j | 0.0773 | W / km
Zero sequence impedance of cable conductor (Zcond0) | 0.2062 | + j | 0.1142 | W / km
Zero sequence sheath resistance (Rsh0) | 2.6612 | W / km
Effective zero sequence impedance of the general mass of earth (Zg0) | 0.148 | + j | 2.0779 | W / km
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 0 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Impedance of MEN comprising 48 customer electrodes
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km.
MEN impedance of 48 customer LV distribution network. (See HB219 Worked Example 4.2.1 for the derivation of this value). | ZMEN = | 0.133 | + j | 0.036 | Ω
Description of distribution transformer earthmat | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance formula | Re = | 0.1346 | r
Cable sheath termination earthing resistance | RCE = | 0.43 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance.
Calculated Values
Equivalent hemispherical radius of the distribution transformer earthmat |  |  |  | 1.1824 | m
Fault current (returning through the earth) |  |  |  | 2257.0394 | A
EPR on the distribution transformer earthmat |  |  |  | 282.9389 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault at the pad mounted distribution transformer
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 6350 | V
Single phase fault level | S = | 200 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 0.6048375j | Ω |  | 0.60484
Negative sequence source impedance | ZS2 = | ZS1 | = | 0.6048375j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 0.6048375j | Ω
HV Overhead Line Data
Conductor Size |  | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | L = | 2 | km
Positive sequence line impedance | ZL1 = | 0.2722+0.3407j |  | W / km
Negative sequence line impedance | ZL2 = | ZL1 = | 0.2722+0.3407j |  | W / km
Zero sequence line impedance | ZL0 = | 0.4204+1.6545j |  | W / km
HV Cable Data
Cable size and type |  | 150 sqmm Al Belted PILCPS
Length | C = | 0.5 | km
Positive sequence cable impedance | ZC1 = | 0.2078+0.0773j |  | W / km
Negative sequence cable impedance | ZC2 = | ZL1 = | 0.2078+0.0773j |  | W / km
Zero sequence impedance of cable conductor (Zcond0) | Zcond0 = | 0.2062+0.1142j |  | W / km
Zero sequence sheath resistance (Rsh0) | Rsh0 = | 2.6612 |  | W / km
Effective zero sequence impedance of the general mass of earth (Zg0) | Zg0 = | 0.148+2.0779j
NER and Earth Impedances
Neutral Earthing Resistor resistance | ZNER = | 0 | Ω
Zone Substation earthmat resistance | RZS = | 0.01 | Ω
Surface soil resistivity | r = | 10 | Ω - m
Impedance of MEN comprising 48 customer electrodes
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km.
MEN impedance of 48 customer LV distribution network. (See HB219 Worked Example 4.2.1 for the derivation of this value). | ZMEN = | 0.133+0.036j |  | Ω
Description of distribution transformer earthmat |  | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance | Re = | 0.1346 | r
| = | 1.346 | Ω
Equivalent Hemispherical Radius | rE =
| = | 1.1824 | m
Cable sheath termination earthing resistance | RCE = | 0.43 | r
| = | 4.3 | Ω
Equivalent MEN plus Re impedance | Zeq =
| = | 0.121765218022997+0.0297988182225639j
Network Impedances
Sequence network impedances | Zpos = | ZS1 + ZL1.L + ZC1.C
| = | 0.6483+1.3248875j |  | Ω
| Zneg = | ZS2 + ZL2.L + ZC2.C
| = | 0.6483+1.3248875j |  | Ω
| Zzero = | [5 empty] | 0.507328162291296+1.0555361462455j
0.0702711059266651
| = | 1.4812281622913+5.0264736462455j |  |  |  | Ω | 0.299626051008975-0.769600129777205j
Fault Current
Zero sequence fault current | I0 =
| = | 264.689551257931-731.44294420396j |  |  |  | A
Zero sequence fault current returning via the earth | Ig0 =
14.2306
| = | 200.99940958148-724.999630793585j |  |  |  |  | 0.439295654068991+1.12834645466769j
Fault current (returning through the earth) | If = | 3.Ig0
| │If │ = | 2257.0394 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Zeq
| = | 282.9389 | V