## Cover Sheet
Extensive Urban MEN System supplied by an HV Overhead Line
HB 219 Worked Example 3.6.1
11 kV source, no NER, 1 km aerial 11 kV feed to a pole-mounted distribution transformer, no OHEW, common HV/LV earth, extensive MEN, LV neutral not bonded to HV source substation.
Extensive urban MEN network supplied by an HV overhead line. HV single phase-to-earth fault at the distribution transformer.
HV Fault Source Data
HV phase - neutral voltage | 6350 | V
Single phase fault level | 200 | MVA
HV Overhead Line Data
Conductor size | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | 1 | km
Positive sequence line impedance | 0.2722 | + j | 0.3407 | W / km
Zero sequence line impedance | 0.4204 | + j | 1.6545 | W / km
NER and Earth Impedance Data
Neutral Earthing Resistor resistance | ZNER = | 0 | W
Zone Substation earthmat resistance | RZS = | 0.01 | W
Surface soil resistivity | r = | 10 | W - m
Impedance of typical urban extensive MEN system
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km. The MEN system extends in both directions from the distribution transformer.
MEN impedance of typical urban extensive MEN system (See HB 219 Worked example 4.1.1 for the derivation of this value). | 0.103 | + j | 0.076 | W / km
Description of distribution transformer earthmat | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance formula | Re = | 0.1346 | r
Assumptions Made
1. Source impedance is purely reactive.
2. Positive sequence source impedance = negative sequence source impedance = zero sequence source impedance
Calculated Values
Equivalent hemispherical radius of the distribution transformer earthmat |  |  |  | 1.1824 | m
Fault current (returning through the earth) |  |  |  | 4201.0304 | A
EPR on the distribution transformer earthmat |  |  |  | 498.8376 | V

## Calculations
Calculations
Symmetrical components network for a HV single phase-to-earth fault at the distribution transformer
HV Fault Source Data
HV phase - neutral voltage | VS1 = | 6350 | V
Single phase fault level | S = | 200 | MVA
Assume source impedance is purely reactive.
Positive sequence source impedance | ZS1 = |  | = | 0.6048375j | Ω |  | 0.60484
Negative sequence source impedance | ZS2 = | ZS1 | = | 0.6048375j | Ω
Zero sequence source impedance | ZS0 = | ZS1 | = | 0.6048375j | Ω
HV Overhead Line Data
Conductor Size |  | Dog (6/4.72mm Al, 7/1.57mm Steel ASCR)
Length | L = | 1 | km
Positive sequence line impedance | ZL1 = | 0.2722+0.3407j |  | W / km
Negative sequence line impedance | ZL2 = | ZL1 = | 0.2722+0.3407j |  | W / km
Zero sequence line impedance | ZL0 = | 0.4204+1.6545j |  | W / km
NER and Earth Impedances
Neutral Earthing Resistor resistance | ZNER = | 0 | Ω
Zone Substation earthmat resistance | RZS = | 0.01 | Ω
Surface soil resistivity | r = | 10 | Ω - m
Impedance of typical urban extensive MEN system
Each customer has one 1.8m deep copper clad 12mm diameter electrode. 4 customers are supplied from each pole, and the LV span length between poles is 50m. The deep layer soil resistivity is assumed to be 100 Ω-m. The LV neutral is a DOG conductor with a self impedance of 0.322 + 0.757j Ω/km. The MEN system extends in both directions from the distribution transformer.
MEN impedance of typical urban extensive MEN system (See HB 219 Worked example 4.1.1 for the derivation of this value). | ZMEN = | 0.103+0.076j |  |  | Ω
Description of distribution transformer earthmat |  | 4 x 1.8m earth rods (12mm dia.) at 1.8m spacing, connected by bare 16mm2 earth wire
Distribution transformer earthmat earth resistance | Re = | 0.1346 | r
| = | 1.346 | Ω
Equivalent Hemispherical Radius | rE =
| = | 1.1824 | m
Equivalent MEN plus Re impedance | Zeq =
| = | 0.0991085957526847+0.0653994111268433j
Network Impedances
Sequence network impedances | Zpos = | ZS1 + ZL1.L
| = | 0.2722+0.9455375j |  | Ω
| Zneg = | ZS2 + ZL2.L
| = | 0.2722+0.9455375j |  | Ω
| Zzero = | ZS0 + ZL0.L + 3.Req + 3.Rzs
| = | 0.747725787258054+2.45553573338053j |  |  | Ω
Fault Current
Zero sequence fault current (returning through the earth) | I0 =
Fault current (returning through the earth) | If = | 3.I0
| = | 1197.07525248792-4026.86812107486j |  |  |  | A
| │If │ = | 4201.0304 | A
EPR
EPR on the distribution transformer earthmat | EPRdt = | If.Zeq
| = | 498.8376 | V