## Cover Sheet
MEN Impedance of a Typical New Zealand Isolated Urban 48 Customer MEN System (without Pole Earthing)
HB 219 Worked Example 4.2.1
Aerial HV and LV lines, 48 LV customers supplied by the distribution transformer, no conductive poles bonded to the LV neutral, no bonding of the LV neutral to any adjacent distribution transformer service areas, LV neutral not bonded to the source zone substation earthing system.
MEN System Data
Neutral conductor type and size |  | DOG (6/4.72mm aluminium with 7/1.57mm steel)
Resistance of the neutral conductor | Rn = | 0.2722 | Ω/km
Diameter of the neutral conductor | d = | 14.2 | mm
LV neutral span length | L = | 0.05 | km
Frequency | f = | 50 | Hz
Deep layer soil resistivity | ρd = | 100 | Ω-m
Surface soil resistivity | ρ = | 10 | Ω-m
Description of customer electrode |  | 1 x 1.8m earth rod (12mm dia.)
Customer single earth rod earth resistance | RCE (ρ) = | 0.552 | r
Number of customers served by each pole | n = | 4
Calculated MEN Impedance
Total MEN impedance | ZMEN = | 0.133 | + j | 0.036249 | Ω
Magnitude of the MEN impedance | │ZMEN│ = | 0.13785 | Ω
Angle of the MEN impedance | arg(ZMEN) = | 15.2458 | deg

## Calculations
Calculations
Aerial HV and LV lines, 48 LV customers supplied by the distribution transformer, no conductive poles bonded to the LV neutral, no bonding of the LV neutral to any adjacent distribution transformer service areas, LV neutral not bonded to the source zone substation earthing system.
Calculation of the Self Impedance of the Neutral Conductor
Conductor type and size |  | DOG (6/4.72mm aluminium with 7/1.57mm steel)
Resistance of the neutral conductor | Rn = | 0.2722 | Ω/km
Frequency | f = | 50 | Hz
Deep layer soil resistivity | ρd = | 100 | Ω-m
Diameter of the neutral conductor | d = | 14.2 | mm
GMR of the neutral conductor | GMRn =
| = | 5.4528 | mm
Self impedance of the neutral conductor | Zsn = |  |  |  |  | 0.32161
5.2324
| = | 0.32161+0.75686147327047j |  | Ω/km |  | 0.75686
Calculation of the Equivalent MEN Impedance using the Ladder Network Equation.
LV neutral span length | L = | 0.05 | km
The self impedance of the neutral conductor of span length L | ZS = | Zsn.L
| = | 0.0160805+0.0378430736635235j |  |  | Ω
| │ZS│ = | 0.041118 | Ω
Surface soil resistivity | ρ = | 10 | Ω-m
Description of customer electrode |  | 1 x 1.8m earth rod (12mm dia.)
Customer single earth rod earth resistance | RCE (ρ) = | 0.552 | r
| = | 5.52 | Ω
Number of customers served by each pole | n = | 4
The earth impedance of 4 customers | ZE =
| = | 1.38 | Ω
Earth impedance of the MEN, looking away from the distribution transformer, at the first pole from the far end | Z1 = | ZE
| = | 1.38 | Ω
At the second pole from the far end | Z2 =
| = | 0.694124292537905+0.00934974505296562j |  |  | Ω
At the third pole from the far end | Z3 =
| = | 0.469357322447966+0.0205605665773211j |  |  | Ω
At the forth pole from the far end | Z4 =
| = | 0.360113356334603+0.031930891454163j |  |  | Ω
At the fifth pole from the far end | Z5 =
| = | 0.297318464635154+0.0430151736436306j |  |  | Ω
At the sixth pole from the far end | Z6 =
| = | 0.257956150577316+0.0535765646258313j |  |  | Ω
If the distribution transformer is located midway in the pole span, the earth impedance of the MEN circuit looking in one direction from the distribution transformer will be | ZN = | (0.5*ZS) + Z6
| = | 0.265996400577316+0.0724981014575931j |  |  | Ω
This is the impedance looking in one direction only. At a distribution transformer with overhead distribution this MEN network normally extends in both directions (on one side of the street only). Therefore the total MEN impedance is half the above value.
Total MEN impedance | ZMEN = | 0.132998200288658+0.0362490507287966j |  |  | Ω
Magnitude of the MEN impedance | │ZMEN│ = | 0.13785 | Ω
Angle of the MEN impedance | arg(ZMEN) = | 15.2458 | deg